## Slide 1: OSID New features on V3.00.4

## Slide 2: Site data info
Shows the initial settings of the Imager at last start up
The initial reference level information is convenient for predicting the date of the next maintenance.

## Slide 3: New log features
Export to .csv
Tool that allows export of alarms, faults, etc. to an Excel file for further and easier analysis, filtering and reporting
View event log graph
Convenient to jump straight from the log to the associated graph to visualize the events in that history block
View a single particular event from the log (*).
Double click anywhere in the specific line and the graph will open with just this event
(*)

## Slide 4: Event log overwritten
Message indicating that the event log was full and has been overwritten with new events
The log itself may contain only few alarms and faults but has been overwritten because of the many ‘significant changes’ exceeding the 10k entries

## Slide 5: Grey levels
Select UV/IR grey levels
Indicates the quality of Emitter alignment
Values need to be more that the minimum of 1600 levels

## Slide 6: Reference levels
Select reference levels
Indicates the current value of the reference level
Compare to the initial reference levels to predict maintenance intervals

## Slide 7: END